## 20-Min Chart
Positive Pressure Fire Rating (Cat. A) | Core Type | Single MAXIMUM OPENING SIZE | Single Egress Pair 2-, 3-, 4- Point Latching MAXIMUM OPENING SIZE | Double Egress Pair 2-, 3-, 4- Point Latching MAXIMUM OPENING SIZE | Metal Vision Panel MAX VISIBLE Wa | Metal Vision Panel MAX VISIBLE La | Metal Vision Panel MAX VISIBLE SIZEa | Wood Lite Kit MAX VISIBLE Wa | Wood Lite Kit MAX VISIBLE La | Wood Lite Kit MAX VISIBLE SIZEa | Fusible Link Louverf | Product Notes
20-min | Particleboard PC-3 | 48" X 120"q | 96" X 108" (2-pt)q; 96" X 108" (3-pt)q; 96" X 120" (4-pt)q | 96" X 108" (2-pt)q; 96" X 108" (3-pt)q; 96" X 120" (4-pt)q | 36" | 54" | 1296" sq. in. | 36" | 54" | 1296" sq. in. | NA | Listed and labeled glass required; CVR/CVC device not allowed; No concealed hardware where additional blocking is required;
20-min | Particleboard PC-5 | 48" X 120"ghi | 96" X 108" (2-pt)cgk; 96" X 108" (3-pt)gk; 96" X 120" (4-pt)cgk | 96" X 108" (2-pt)cgk; 96" X 108" (3-pt)gk; 96" X 120" (4-pt)cgk | 36" | 54" | 1296" sq. in. | 36"bp | 54"bp | 1296"sq. in.bp | NA | Listed and labeled glass required; CVR/CVC device allowede; Dutch door availablel; Removable edge availablem
20-min | Structural Composite Lumber SCLC-5 | 48" X 120"ghi | 96" X 108" (2-pt)cgk; 96" X 108" (3-pt)gk; 96" X 120" (4-pt)cgk | 96" X 108" (2-pt)cgk; 96" X 108" (3-pt)gk; 96" X 120" (4-pt)cgk | 36" | 92" | 2950 sq in. | 36"; 37"(48"x96") 30"(48"x108") | 54"; 79-3/4"(48"x96") 92"(48"x108") | 1296 sq. in. bpr(48" x 120") 2950 sq in. r(48"X96") 2760 sq in. r(48"X108") | NA | Listed and labeled glass required; CVR/CVC device allowede; Dutch door availablel ; Removable edge availablem
20-min | Agrifiber WSPC-5 | 48" X 120"ghi | 96" X 108" (2-pt)cgk; 96" X 108" (3-pt)gk; 96" X 120" (4-pt)cgk | 96" X 108" (2-pt)cgk; 96" X 108" (3-pt)gk; 96" X 120" (4-pt)cgk | 36" | 54" | 1296" sq. in. | 36" | 54" | 1296"sq. in.bp | NA | Listed and labeled glass required; CVR/CVC device allowede; Dutch door availablel; Removable edge availablem
20-min | Lead Lined PC/SCLC/WSPC LL-5 | 48" X 108" | 96" X 108" (2-pt)q; 96" X 108" (3-pt)q; 96" X 108" (4-pt)q | 96" x 96"q | 16" | 16" | 256" sq. in. | NA | NA | NA | NA | Listed and labeled glass required; CVR/CVC device not allowed DE Pairs - Neenah Facility
aGlass and kit combinations subject to approved fire listing & VT maximums shown above.
bDivided lites available. Consult VT for sizes and approvals - Neenah facility.
cMaximum opening height with CVC or CVC LBL is 96".
e5" metal channel required - Holstein facility. 5" metal channel optional (clips required) - Neenah facility.
fLouvers are not available in 20-minute doors. See Product Update P321.
gMaximum transom height 40".
hTotal door/transom unit not to exceed total of 48" x 120" unless Transom Bar in Frame.
iIf Rabbeted Door/Transom, Transom bar is required between the door and the transom panel when operational hardware such as closers or strikes are used (door cannot latch into transom panel).
kTransom Bar in Pairs required. Single Transom over Pair - Neenah facility. Split Transoms Maximum Transom Width 48" (Door Width) - Holstein or Neenah facility.
lSubject to latching, intumescent, and astragal requirements.
mRemovable vinyl or stainless steel edge available - Neenah facility.
pFlat wood panel available. Single panel maximum 36"W x 54H for all door types, multiple panels allowed. Particleboard & Agrifiber core cannot exceed 1296 sq inches total. SCLC available with multiple panels up to 2774 sq inches total with any one panel maximum not to exceed 38"L x 49"H - Neenah facility.
qTransoms not allowed
rDoor height up to 96" maximum visible lite 37"x79-3/4" (max 2950 sq in.); door height up to 108" maximum visible lite 30"x92" (max 2760 sq in.); door height up to 120" maximum visible lite 36"x54" (max 1296 sq in.)
Notes:
Hinges & Pivots - Per NFPA 80 Table 6.4.3.1;
Locks - Cylinder, Mortised, (max. 5" backset) & Deadbolt;
Closers - Surface allowed; Concealed allowed, see P151F
Viewers - Maximum 2 per door; 1" Diameter;
Auto Door Bottoms - Mortised, Surface & Semi-mortised;
Kick Plates - Surface Maximum 48" high;
3-point Fire Rated Pairs - Only flush bolts are approved for inactive leaf
Fire Pins are not allowed as a point of latching. Fire pins are auxilary latches.
Plant-on moulding allowed - See P113F
Listed Metal Edges & Astragals allowed for wood doors
Open Back Strikes - not allowed
Reveals allowed - See P264
Surface applied mirrors allowed. Recessed or flush mirrors are not allowed.
Fire approvals apply to all face materials offerings
Intertek/Warnock Hersey (WHI) listed and labeled
1-3/4" approvals listed. Contact VT for additional thickness approvals.
Removable edges allowed, Stainless steel or Vinyl. Singles or Pairs at 20-minutes.
Lite / Lock Margins - See P256

## 45-, 60-, 90-Min Chart
Positive Pressure Fire Rating (Cat. A) | Core Type | Single MAXIMUM OPENING SIZE | Single Egress Pair 2-, 3-, 4- Point Latching MAXIMUM OPENING SIZE | Double Egress Pair 2-, 3-, 4- Point Latching MAXIMUM OPENING SIZE | Metal Vision Panel MAX VISIBLE Wa | Metal Vision Panel MAX VISIBLE La | Metal Vision Panel MAX VISIBLE SIZE a | Wood Lite Kit MAX VIS Wa | Wood Lite Kit MAX VIS La | Wood Lite Kit MAX VIS SIZEa | Fusible Link Louver MAX W | Fusible Link Louver MAX L | Fusible Link Louver MAX SIZE | Product Notes
45-Min | Particleboard PC-5 | 48" x 96"f | 72" x 84" | N/A | 24" | 54" | 1296 sq. in. | N/A | N/A | N/A | 24" | 24" | 576 sq. in. | Listed and labeled glass required; CVR/CVC device not allowed; Neenah Facility
45-Min | Structural Composite Lumber SCLC-5 | 36" x 84"f | N/A | N/A | 24" | 54" | 864 sq. in. | N/A | N/A | N/A | 24" | 24" | 576 sq. in. | Listed and labeled glass required; LBL devices are not allowed; CVR/CVC device not allowed; Holstein Facility
45-Min | Arifiber WSPC-5 | 48" x 120" | 96" x 96" | 96" x 96" | 36"d | 54" | 1296 sq. in. | N/A | N/A | N/A | 24" | 36" | 864 sq. in.b | Listed and labeled glass required; CVR/CVC LBL not allowed; CVR allowede; CVC allowed up to 96"e; SVR LBL not allowed on DE; SVR LBL allowed on SE up to 72" x 84"; Transoms Neenah Facility
45-Min | Fire Composite FD-5 | 48" x 108"ghi | 96" x 108"cgk | 96" x 108"gkp | 30-3/4" | 70-3/4" | 2176 sq. in. | 30-3/4" | 70-3/4" | 2176 sq. in. | 24" | 36"b | 864 sq. in.b | Listed and labeled glass required; CVR/CVC device allowede Removable edge availablem Max Height for DE 96" - Holstein FacilityP
60-Min | Fire Composite FD-5 | 48" x 108"ghi | 96" x 108"cgk | 96 x 96gk | 24"l 36"o | 40"l 56"o | 960 sq. in.l 1344 sq. in.o | 10" | 33" | 100" | 24" | 36"b | 864 sq. in.b | Listed and labeled glass required; CVR/CVC device allowede; Electric strikes not allowed Removable edge available (singles only)m
90-Min | Fire Composite FD-5 | 48 x 108ghi | 96 x 108cgk | 96 x 96gk | 24"l 36"o | 40"l 56"o | 960 sq. in.l 1344 sq. in.o | 10"n | 33"n | 100"n | 24" | 36"b | 864 sq. in.b | Listed and labeled glass required; CVR/CVC device allowede; Electric strikes not allowed; SVR LBL allowed on DE pairs up to 84" Removable edge available (singles only)m
45-Min | Lead Lined LL-5 | 48 x 96f | N/A | N/A | 16" | 33" | 256 sq. in. | N/A | N/A | N/A | N/A | N/A | N/A | Listed and labeled glass required; CVR/CVC not allowed
aGlass and kit combinations subject to approved fire listing & VT maximums shown above. 100 sq inch maximum visible glass for temp rise ratings.
bMaximum Louver 24" W X 30" L (720 sq. inches) for L-1900 FR fusible link louver.
cMaximum opening height with CVC or CVC LBL is 96".
dCeramic or wire glass required for Metal Vision Panels; Maximim 24" W x 54" L for wire glass.
e5" metal channel required - Holstein Facility. 5" metal channel optional at Fire Composite (FD-5) 45-minute doors (clips and 2 fire pins required) - Neenah Facility.
fTransoms not allowed.
gMaximum transom height 40".
hTotal door/transom unit not to exceed total of 48" x 108" unless Transom Bar in Frame.
iIf Rabbeted Door/Transom, Transom bar is required between the door and the transom panel when operational hardware such as closers or strikes are used (door cannot latch into transom panel).
kTransom Bar in Pairs required. Single Transom over Pair - Neenah facility. Split Transoms Maximum Transom Width 48" (Door Width) - Holstein or Neenah facility.
lMaximum cut out lite size.
mRemovable vinyl or stainless steel edge available - Neenah facility.
nVT1FM woodstops. Factory Installation Required - Neenah facility.
oAMS #118D or #120, factory installation of MVP and ceramic glass required. Multiple lites allowed, total cannot exceed sizes listed - Neenah facility.
P Double Egress Maximum height 108" - Neenah Facility; Double Egress Maximum height 96" - Holstein Facility
Notes:
Hinges & Pivots - Per NFPA 80 Table 6.4.3.1;
Locks - Cylinder, Mortised, (max. 5" backset) & Deadbolt;
Closers - Surface allowed; Concealed allowed, see P151F
Viewers - Maximum 2 per door; 1" Diameter;
Auto Door Bottoms - Mortised, Surface & Semi-mortised;
Kick Plates - Surface Maximum 48" high;
3-point Fire Rated Pairs - Only flush bolts are approved for inactive leaf
Fire Pins are not allowed as a point of latching. Fire pins are auxilary latches.
Plant-on moulding allowed - See P113F
Listed Metal Edges & Astragals allowed for wood doors
Open Back Strikes - not allowed
Reveals allowed - See P264
Surface applied mirrors only allowed at 45-minute with Fire Composite core. Recessed or flush mirrors are not allowed.
Fire approvals apply to all face materials offerings
Intertek/Warnock Hersey (WHI) listed and labeled
1-3/4" approvals listed. Contact VT for additional thickness approvals.
Removable edges allowed, Stainless steel or Vinyl. Singles/Pair at 45-minutes. Singles at 60-90-minutes.
Lite / Lock Margins - See P256

## Fire Pin Chart
Fire Rating | Door Type | Max Size | Exit Device | Egress | Aux Fire Pin
90-minutes | FD-5 | 8'0" X 7'0" | CVR LBR | Single / Double | No
60-minutes | FD-5 | 8'0" X 7'0" | CVR LBR | Single / Double | No
45-minutes | FD-5 | 8'0" X 7'0" | CVR LBR | Single / Double | No
20-minutes | PC-5, SCLC-5, WSPC-5 | 8'0" X 7'0" | CVR LBR | Single / Double | No
90-minutes | FD-5 | 8'0" X 7'0" | CVC LBL | Single / Double | No
60-minutes | FD-5 | 8'0" X 7'0" | CVC LBL | Single / Double | No
45-minutes | FD-5 | 8'0" X 7'0" | CVC LBL | Single / Double | No
20-minutes | PC-5, SCLC-5, WSPC-5 | 8'0" X 7'0" | CVC LBL | Single / Double | No
90-minutes | FD-5 | 8'0" X 7'0" | SVR LBR | Single | No
60-minutes | FD-5 | 8'0" X 7'0" | SVR LBR | Single / Double | No
45-minutes | PC-5* | 6'0" X 7'0" | SVR LBR | Single | 1 - Door to Door
45-minutes | WSPC-5 | 6'0" X 7'0" | SVR LBR | Single | No
45-minutes | FD-5 | 8'0" X 7'0" | SVR LBR | Single / Double | No
20-minutes | PC-5, SCLC-5, WSPC-5 | 8'0" X 7'0" | SVR LBR | Single / Double | No
90-minutes | FD-5 | 8'0" X 7'0" | SVR LBR | Double | 2 - Door to Door
90-minutes | FD-5 | 8'0" X 9'0" | SVR LBR | Single | 1 - Door to Door
60-minutes | FD-5 | 8'0" X 8'0" | SVR LBR | Double | 1 - Door to Door
60-minutes | FD-5 | 8'0" X 9'0" | SVR LBR | Single | 1 - Door to Door
45-minutes | FD-5 | 8'0" X 8'0" | SVR LBR | Double | 1 - Door to Door
45-minutes | FD-5 | 8'0" X 9'0" | SVR LBR | Single | 1 - Door to Door
20-minutes | PC-5, SCLC-5, WSPC-5 | 8'0" X 8'0" | SVR LBR | Double | 1 - Door to Door
20-minutes | PC-5, SCLC-5, WSPC-5 | 8'0" X 9'0" | SVR LBR | Double | 2 - Door to Door
20-minutes | PC-5, SCLC-5, WSPC-5 | 8'0" X 9'0" | SVR LBR | Single | 1 - Door to Door
90-minutes | FD-5 | 8'0" X 8'0" | CVC LBL | Single / Double | 1 - Door to Door
60-minutes | FD-5 | 8'0" X 8'0" | CVR LBR | Double | 1 - Door to Door
90-minutes | FD-5 | 8'0" X 8'0" | CVR LBR | Double | 1 - Door to Door
60-minutes | FD-5 | 8'0" X 8'0" | CVC LBL | Single / Double | 1 - Door to Door
45-minutes | FD-5 | 8'0" X 8'0" | CVC LBL | Single / Double | 1 - Door to Door
20-minutes | PC-5, SCLC-5, WSPC-5* | 8'0" X 8'0" | CVC LBL | Single / Double | 2 - Door to Door (No Channel)
45-minutes | FD-5* | 8'0" X 8'0" | CVC LBL | Single / Double | 2 - Door to Door (No Channel)
20-minutes | PC-5, SCLC-5, WSPC-5 | 8'0" X 8'0" | CVC LBL | Single / Double | 1 - Door to Door
90-minutes | FD-5 | 8'0" X 9'0" | CVR LBR | Single | 1 - Door to Door
60-minutes | FD-5 | 8'0" X 9'0" | CVR LBR | Single | 1 - Door to Door
45-minutes | FD-5 | 8'0" X 9'0" | CVR LBR | Single / Double | 1 - Door to Door
20-minutes | PC-5, SCLC-5, WSPC-5* | 8'0" X 9'0" | CVR LBR | Single / Double | 2 - Door to Door (No Channel)
45-minutes | FD-5* | 8'0" X 9'0" | CVR LBR | Single / Double | 2 - Door to Door (No Channel)
20-minutes | PC-5, SCLC-5, WSPC-5 | 8'0" X 9'0" | CVR LBR | Single / Double | 1 - Door to Door
45-minutes | FD-5 | 8'0" X 9'0" | SVR LBR | Double | 2 - Door to Door
Notes:
Fire pins required as stated for 2-pt latching pairs. Not available for 3- or 4-pt latching pair approvals.
Fire pin shall be minumum of 4" from the bottom of the door and maximum of 24" from the bottom.
Fire pin must be a minimum of 5" from any other hardware prep.
Maximum 20" between top and bottom pin when required.
Fire pins to be installed door-to-door.
Fire pin requirements applicable to multi-point locks
*Neenah Facility Only